## How to fill
How to fill this workbook
Each sheet is one level of the plant: Plant › Areas › Machines › Parts › Sensors.
Columns marked * are needed. Hover a column title for what it means.
Plant: fill the Value column.
Areas: one row per factory, section, line or building. 'Inside area' names the area it sits in.
Machines: one row per machine. 'Area' names an area from the Areas sheet.
Parts: one row per part of a machine. Parts named on the Sensors sheet are added too.
Sensors: one row per sensor. 'Machine code' and 'Part' place it on its machine.
Uploading again updates rows with the same area name, machine code, part name or sensor tag;
an empty cell keeps what the onboarding already holds, and nothing is removed.
Everything stays editable on the onboarding steps until the plant is created.

## Plant
Field | Value | What to write
Name * | Demo Copper Concentrator | The plant's full name
Code * | DCC-01 | Short code: letters, digits and dashes (e.g. LUM-04)
Short name | Copper concentrator | Name used where space is tight
Region | Zambia | Country or region
Location | Chingola, Copperbelt | Town or address
Coordinates | -12.53, 27.85 | Latitude, longitude
Time zone * | Africa/Lusaka | As Region/City (e.g. Africa/Lusaka)
Description | Copper sulphide ore concentrator: crushing, grinding and flotation | What the plant makes
Design capacity | 1,200 t/h ore | e.g. 3,000 t/day clinker

## Areas
Area * | Inside area
Concentrator
Crushing | Concentrator
Grinding | Concentrator
Flotation | Concentrator
Tailings
Note on A1: A factory, section, line or building of the plant
Note on B1: The area it sits in; leave empty when it sits directly under the plant

## Machines
Machine code * | Machine name * | Area | Type | Manufacturer | Model | Power rating | Operating speed | Importance
CRU-01 | Primary gyratory crusher | Crushing | gyratory crusher | Metso | Superior MK-III 60-110 | 750 kW | 600 rpm | A (Critical)
CNV-01 | Crushed ore conveyor | Crushing | belt conveyor |  |  | 315 kW | 1490 rpm | B (Essential)
MIL-01 | SAG mill | Grinding | semi-autogenous grinding mill | FLSmidth | 36 ft x 17 ft | 13,000 kW | 9.8 rpm | A (Critical)
MIL-02 | Ball mill | Grinding | ball mill | FLSmidth | 24 ft x 39 ft | 11,000 kW | 12.5 rpm | A (Critical)
PMP-01 | Cyclone feed pump | Grinding | centrifugal slurry pump | Weir | Warman 650 MCR | 1,000 kW | 360 rpm | B (Essential)
BLW-01 | Flotation air blower | Flotation | centrifugal blower | Atlas Copco | ZB 160 | 160 kW | 2980 rpm | B (Essential)
PMP-02 | Tailings pump | Tailings | centrifugal slurry pump | Weir | Warman 450 TU | 560 kW | 450 rpm | C (General)
Note on A1: The plant's own equipment code (e.g. KLN-01)
Note on B1: e.g. Rotary kiln
Note on C1: Name of an area from the Areas sheet; empty = directly under the plant
Note on D1: Plain kind (e.g. rotary kiln, vacuum casting cell)
Note on G1: e.g. 315 kW
Note on H1: e.g. 3.5 rpm
Note on I1: A (Critical), B (Essential) or C (General); empty = B

## Parts
Machine code * | Part *
CRU-01 | Main shaft
CRU-01 | Eccentric
CRU-01 | Lube oil system
CRU-01 | Drive motor
CNV-01 | Head pulley
CNV-01 | Tail pulley
CNV-01 | Belt
CNV-01 | Drive motor
MIL-01 | Feed trunnion bearing
MIL-01 | Discharge trunnion bearing
MIL-01 | Girth gear and pinion
MIL-01 | Lube oil system
MIL-01 | Drive motor
MIL-02 | Feed trunnion bearing
MIL-02 | Discharge trunnion bearing
MIL-02 | Shell
MIL-02 | Drive motor
PMP-01 | Pump casing
PMP-01 | Pump bearing housing
PMP-01 | Gland seal
PMP-01 | Drive motor
BLW-01 | Impeller bearing
BLW-01 | Discharge header
BLW-01 | Inlet filter
BLW-01 | Drive motor
PMP-02 | Pump casing
PMP-02 | Pump bearing housing
PMP-02 | Drive motor
Note on A1: Code from the Machines sheet
Note on B1: A part of the machine (e.g. Inlet seal, Main drive)

## Sensors
Tag * | Sensor name | Machine code * | Part * | Location | Measures | Unit | Reading kind | Origin | Signal type | Range from | Range to | Normal from | Normal to | LL | L | H | HH | Priority | Remarks
TT-CRU-101 | Lube oil supply temperature | CRU-01 | Lube oil system | Supply line | Temperature | °C | Number | Online | RTD PT100 | 0 | 100 | 35 | 50 |  | 30 | 55 | 60 | High
PT-CRU-102 | Lube oil supply pressure | CRU-01 | Lube oil system | Supply line | Pressure | bar | Number | Online | 4-20 mA | 0 | 10 | 2 | 4 | 1 | 1.5 |  |  | High
ZT-CRU-103 | Main shaft position | CRU-01 | Main shaft | Hydroset cylinder | Position / displacement | mm | Number | Online | 4-20 mA | 0 | 100 | 20 | 60 |  | 10 | 70 | 80 | Medium | Sets the closed-side setting
IT-CRU-104 | Drive motor current | CRU-01 | Drive motor |  | Electrical current | A | Number | Online | 4-20 mA | 0 | 120 | 40 | 90 |  |  | 100 | 110 | Medium
VT-CRU-105 | Drive motor DE bearing vibration | CRU-01 | Drive motor | Drive end | Vibration velocity | mm/s | Number | Online | 4-20 mA | 0 | 25 | 0 | 4.5 |  |  | 7.1 | 11 | High
ZS-CRU-106 | Lube oil pump running | CRU-01 | Lube oil system |  | Discrete state |  | On/off | Online | Digital input | [8 empty] | High
ST-CNV-101 | Head pulley speed | CNV-01 | Head pulley |  | Rotational speed | rpm | Number | Online | Pulse | 0 | 120 | 80 | 95 | 70 | 75 |  |  | High | Belt slip detection
IT-CNV-102 | Drive motor current | CNV-01 | Drive motor |  | Electrical current | A | Number | Online | 4-20 mA | 0 | 60 | 20 | 45 |  |  | 50 | 55 | Medium
TT-CNV-103 | Head pulley bearing temperature | CNV-01 | Head pulley | Drive side bearing | Temperature | °C | Number | Online | RTD PT100 | 0 | 150 | 30 | 70 |  |  | 85 | 95 | Medium
ZS-CNV-104 | Belt misalignment switch | CNV-01 | Belt | Tail end | Discrete state |  | On/off | Online | Digital input | [8 empty] | High
WT-CNV-105 | Belt scale feed rate | CNV-01 | Belt | Weigh frame | Flow | t/h | Number | Online | 4-20 mA | 0 | 1500 | 900 | 1300 |  | 600 | 1400 | 1450 | Medium
TT-MIL-101 | Feed trunnion bearing temperature | MIL-01 | Feed trunnion bearing |  | Temperature | °C | Number | Online | RTD PT100 | 0 | 120 | 35 | 60 |  |  | 70 | 80 | High
TT-MIL-102 | Discharge trunnion bearing temperature | MIL-01 | Discharge trunnion bearing |  | Temperature | °C | Number | Online | RTD PT100 | 0 | 120 | 35 | 60 |  |  | 70 | 80 | High
PT-MIL-103 | Feed trunnion lift oil pressure | MIL-01 | Feed trunnion bearing | Lift pocket | Pressure | bar | Number | Online | 4-20 mA | 0 | 160 | 60 | 110 | 40 | 50 |  |  | High
VT-MIL-104 | Pinion bearing vibration | MIL-01 | Girth gear and pinion | Pinion DE bearing | Vibration velocity | mm/s | Number | Online | 4-20 mA | 0 | 25 | 0 | 4.5 |  |  | 7.1 | 11 | High
TT-MIL-105 | Pinion bearing temperature | MIL-01 | Girth gear and pinion | Pinion DE bearing | Temperature | °C | Number | Online | RTD PT100 | 0 | 120 | 35 | 65 |  |  | 75 | 85 | Medium
JT-MIL-106 | Mill motor power | MIL-01 | Drive motor |  | Electrical power | kW | Number | Online | Modbus | 0 | 14000 | 9000 | 12500 |  |  | 13000 | 13500 | Medium
WT-MIL-107 | Mill load | MIL-01 | Feed trunnion bearing |  | Load | % | Number | Calculated |  | 0 | 100 | 25 | 35 | 18 | 20 | 38 | 40 | High | From bearing pressures
SE-MIL-108 | Mill speed | MIL-01 | Drive motor |  | Rotational speed | rpm | Number | Online | Pulse | 0 | 12 | 9 | 10.5 |  |  |  |  | Low
ZS-MIL-109 | Lube oil pump running | MIL-01 | Lube oil system |  | Discrete state |  | On/off | Online | Digital input | [8 empty] | High
TT-MIL-110 | Lube oil tank temperature | MIL-01 | Lube oil system | Tank | Temperature | °C | Number | Online | RTD PT100 | 0 | 100 | 35 | 50 |  | 30 | 55 | 60 | Medium
LT-MIL-111 | Lube oil tank level | MIL-01 | Lube oil system | Tank | Level | % | Number | Online | 4-20 mA | 0 | 100 | 50 | 90 | 20 | 30 |  |  | Medium
TT-MIL-201 | Feed trunnion bearing temperature | MIL-02 | Feed trunnion bearing |  | Temperature | °C | Number | Online | RTD PT100 | 0 | 120 | 35 | 60 |  |  | 70 | 80 | High
TT-MIL-202 | Discharge trunnion bearing temperature | MIL-02 | Discharge trunnion bearing |  | Temperature | °C | Number | Online | RTD PT100 | 0 | 120 | 35 | 60 |  |  | 70 | 80 | High
JT-MIL-203 | Mill motor power | MIL-02 | Drive motor |  | Electrical power | kW | Number | Online | Modbus | 0 | 12000 | 7000 | 10500 |  |  | 11000 | 11500 | Medium
VT-MIL-204 | Drive motor DE bearing vibration | MIL-02 | Drive motor | Drive end | Vibration velocity | mm/s | Number | Online | 4-20 mA | 0 | 25 | 0 | 4.5 |  |  | 7.1 | 11 | High
MN-MIL-205 | Shell liner thickness | MIL-02 | Shell | Feed end, row 3 | Position / displacement | mm | Number | Manual |  | 0 | 150 | 40 | 120 | 25 | 35 |  |  | Low | Measured at each relining shutdown
PT-PMP-101 | Discharge pressure | PMP-01 | Pump casing | Discharge flange | Pressure | bar | Number | Online | 4-20 mA | 0 | 10 | 3 | 5 |  | 2 | 6 | 7 | High
FT-PMP-102 | Cyclone feed flow | PMP-01 | Pump casing | Discharge line | Flow | m³/h | Number | Online | 4-20 mA | 0 | 6000 | 3500 | 4800 | 2500 | 3000 | 5200 | 5500 | High
TT-PMP-103 | Bearing housing temperature | PMP-01 | Pump bearing housing |  | Temperature | °C | Number | Online | RTD PT100 | 0 | 120 | 30 | 65 |  |  | 75 | 85 | Medium
VT-PMP-104 | Bearing housing vibration | PMP-01 | Pump bearing housing |  | Vibration velocity | mm/s | Number | Online | 4-20 mA | 0 | 25 | 0 | 4.5 |  |  | 7.1 | 11 | High
IT-PMP-105 | Drive motor current | PMP-01 | Drive motor |  | Electrical current | A | Number | Online | 4-20 mA | 0 | 200 | 100 | 160 |  |  | 175 | 190 | Medium
DT-PMP-106 | Slurry solids | PMP-01 | Pump casing | Discharge line | Ratio / share | % | Number | Calculated |  | 0 | 100 | 60 | 68 | 50 | 55 | 72 | 75 | Medium | From density meter
PT-BLW-101 | Air header pressure | BLW-01 | Discharge header |  | Pressure | mbar | Number | Online | 4-20 mA | 0 | 1000 | 550 | 700 | 400 | 500 | 750 | 800 | High
FT-BLW-102 | Air flow | BLW-01 | Discharge header |  | Flow | m³/h | Number | Online | 4-20 mA | 0 | 30000 | 18000 | 24000 |  | 15000 | 27000 |  | Medium
TT-BLW-103 | Impeller bearing temperature | BLW-01 | Impeller bearing |  | Temperature | °C | Number | Online | RTD PT100 | 0 | 150 | 40 | 80 |  |  | 90 | 100 | High
VT-BLW-104 | Impeller bearing vibration | BLW-01 | Impeller bearing |  | Vibration velocity | mm/s | Number | Online | 4-20 mA | 0 | 25 | 0 | 4.5 |  |  | 7.1 | 11 | High
PDT-BLW-105 | Inlet filter differential pressure | BLW-01 | Inlet filter |  | Pressure | mbar | Number | Online | 4-20 mA | 0 | 50 | 5 | 20 |  |  | 25 | 35 | Low | Change filter at H
PT-PMP-201 | Discharge pressure | PMP-02 | Pump casing | Discharge flange | Pressure | bar | Number | Online | 4-20 mA | 0 | 16 | 6 | 10 |  | 4 | 12 | 14 | High
IT-PMP-202 | Drive motor current | PMP-02 | Drive motor |  | Electrical current | A | Number | Online | 4-20 mA | 0 | 120 | 50 | 90 |  |  | 100 | 110 | Medium
TT-PMP-203 | Bearing housing temperature | PMP-02 | Pump bearing housing |  | Temperature | °C | Number | Online | RTD PT100 | 0 | 120 | 30 | 65 |  |  | 75 | 85 | Medium
Note on A1: The sensor's tag, unique in the plant (e.g. TMP-KLN-01)
Note on B1: What it reads (e.g. Inlet gas temperature); empty = the tag
Note on C1: Code from the Machines sheet
Note on D1: The part it sits on; a new name adds the part
Note on E1: Where on the part
Note on F1: What it measures; empty = guessed from tag and unit
Note on G1: e.g. °C, bar, mm/s, A
Note on H1: Number or On/off; empty = Number
Note on I1: Online (wired), Manual (read by hand) or Calculated; empty = Online
Note on J1: e.g. 4–20 mA, RTD PT100, Modbus
Note on K1: Lowest value the sensor can read
Note on L1: Highest value the sensor can read
Note on M1: Lowest value in normal running
Note on N1: Highest value in normal running
Note on O1: Critical low limit
Note on P1: Alert low limit
Note on Q1: Alert high limit
Note on R1: Critical high limit

## Lists (hidden)
Measures | Unit | Importance | Reading kind | Origin
Discrete state | % | A (Critical) | Number | Online
Electrical current | °C | B (Essential) | On/off | Manual
Electrical power | A | C (General) |  | Calculated
Flow | bar
Gas concentration | count
Level | d
Load | dB
Mass | h
Position / displacement | kW
Pressure | L/min
Ratio / share | m³/h
Rotational speed | mbar
Sound level | mg/Nm³
Stroke rate | mm
Temperature | mm/rev
Travel per revolution | mm/s
Vibration acceleration | ppm
Vibration displacement | rpm
Vibration velocity | s
stroke/min
t
t/h
vol%