## Site
Plant name | Plant code | Country | Location | Timezone | Capacity | About
Demo Water Treatment Works | DWT-01 | India | Pune, Maharashtra | Asia/Kolkata | 120 MLD | Conventional treatment: intake, clarification, rapid sand filtration, chlorination

## Sections
Section | Part of
Raw water intake
Treatment plant
Clarification | Treatment plant
Filtration | Treatment plant

## Equipment list
Equipment name | Equipment code | Section | Make | Rating | Criticality | Equipment type
Raw water pump 1 | RWP-01 | Raw water intake | KSB | 450 kW | a | vertical turbine pump
Raw water pump 2 | RWP-02 | Raw water intake | KSB | 450 kW | b | vertical turbine pump
Flash mixer | FLM-01 | Clarification |  | 15 kW | c | flash mixer
Clarifier bridge drive | CLF-01 | Clarification |  | 2.2 kW | b | clarifier scraper drive
Air scour blower | ABB-01 | Filtration | Kirloskar | 75 kW | b | twin-lobe blower
Backwash pump | BWP-01 | Filtration | KSB | 110 kW | b | centrifugal pump
Chlorine dosing skid | CLD-01 | Clear water & pumping |  |  | a | chlorinator
High-lift pump 1 | HLP-01 | Clear water & pumping | KSB | 900 kW | a | horizontal split-case pump

## Instrument list
Tag No. | Equipment | Component | Description | UOM | Quantity | Min | Max | Lo Lo | Lo | Hi | Hi Hi | Signal | Notes
PT-RWP-101 | RWP-01 | Pump | Discharge pressure | bar | Pressure | 0 | 10 | 2 | 3 | 6.5 | 7.5 | 4-20 mA
FT-RWP-102 | RWP-01 | Pump | Discharge flow | m³/h | Flow | 0 | 3,000 | 1,200 | 1,500 | 2,800 | 2,950 | 4-20 mA | Numbers typed as text
IT-RWP-103 | RWP-01 | Motor | Motor current | A | Electrical current | 0 | 800 |  |  | 700 | 760 | 4-20 mA
TT-RWP-104 | RWP-01 | Motor | Motor winding temperature | °C | Temperature | 0 | 200 |  |  | 130 | 145 | RTD PT100
VT-RWP-105 | RWP-01 | Motor | Motor NDE bearing vibration | mm/s | Vib | 0 | 25 |  |  | 7.1 | 11 | 4-20 mA | Quantity written short
PT-RWP-201 | RWP-02 | Pump | Discharge pressure | bar | Pressure | 0 | 10 | 2 | 3 | 6.5 | 7.5 | 4-20 mA
IT-RWP-203 | RWP-02 | Motor | Motor current | A | Electrical current | 0 | 800 |  |  | 700 | 760 | 4-20 mA
VT-RWP-205 | RWP-02 | Motor | Motor NDE bearing vibration | mm/s | Vibration velocity | 0 | 25 |  |  | 7.1 | 11 | 4-20 mA
IT-FLM-101 | FLM-01 | Motor | Mixer motor current | A | Electrical current | 0 | 50 |  |  | 30 | 35 | 4-20 mA
ZS-FLM-102 | FLM-01 | Motor | Mixer running |  | Discrete state | [6 empty] | Digital input
WT-CLF-101 | CLF-01 | Drive | Drive torque | % | Load | 0 | 100 |  |  | 80 | 95 | 4-20 mA | Scraper overload
ZS-CLF-102 | CLF-01 | Drive | Bridge running |  | Discrete state | [6 empty] | Digital input
PT-ABB-101 | ABB-01 | Blower | Discharge pressure | mbar | Pressure | 0 | 1000 |  |  | 600 | 700 | 4-20 mA
TT-ABB-102 | ABB-01 | Blower | Discharge air temperature | °C | Temperature | 0 | 150 |  |  | 110 | 125 | RTD PT100
FT-BWP-101 | BWP-01 | Pump | Backwash flow | m³/h | Flow | 0 | 2,500 |  | 1,200 |  |  | 4-20 mA
PT-BWP-102 | BWP-01 | Pump | Discharge pressure | bar | Pressure | 0 | 6 |  | 1 | 4 | 5 | 4-20 mA
AT-CLD-101 | CLD-01 | Chlorinator room | Chlorine leak detector | ppm | Gas concentration | 0 | 10 |  |  | 0,5 | 1 | 4-20 mA | Decimal comma
WT-CLD-102 | CLD-01 | Tonner scale | Chlorine tonner weight | t | Mass | 0 | 1 | 0.05 | 0.15 |  |  | 4-20 mA
PT-HLP-101 | HLP-01 | Pump | Discharge pressure | bar | Pressure | 0 | 16 |  | 4 | 10 | 12 | 4-20 mA
FT-HLP-102 | HLP-01 | Pump | Delivery flow | m³/h | Flow | 0 | 6,000 |  |  |  |  | 4-20 mA
TT-HLP-103 | HLP-01 | Pump | DE bearing temperature | °C | Temperature | 0 | 120 |  |  | 75 | 85 | RTD PT100
VT-HLP-104 | HLP-01 | Pump | DE bearing vibration | mm/s | Vibration velocity | 0 | 25 |  |  | 7.1 | 11 | 4-20 mA
IT-HLP-105 | HLP-01 | Motor | Motor current | A | Electrical current | 0 | 150 |  |  | 110 | 125 | 4-20 mA
LT-HLP-106 | HLP-01 | Suction | Clear water reservoir level | % | Level | 0 | 100 | 15 | 25 | 95 | 98 | 4-20 mA